# DORMA SPECIFICATION SERVICES

Project

L20/			AUTOMATIC FOLDING DOORS

Manufacturers		DORMA UK LTD.

WILBURY WAY, HITCHIN, SG4 0AB.

Tel: 	+44 (0)1462 477 600,

Email: 	Info@dorma-uk.co.uk

Web: 	www.dorma.com

Operating System	DORMA FFT Flex Green Folding Automatic Door

Thermally broken, double glazed automatic door system. Tested system ‘U’ value between 1.7 and 2.4 W/m2K. Enhanced wind load resistance (depending on door size, up to Beaufort Force 8)

- Microprocessor controlled modular designed

- Adjustable opening and closing speed

- Variable hold open times

- Enhanced wind load control

- Excellent thermal separation

- Safeguarded functionality with self-monitoring sensors

- Suitable for emergency exits and escape routes

- 5 position mode switch (off, automatic, partial opening, exit only and hold open) External operator switch to be lockable and remotely positioned. Internal operator switch to be fitted within the cover.

- Self-regulating safety system monitoring all door movements including closing force.

- Presence sensors monitoring the threshold area preventing the doors from closing on users

- Night/Bank Facility for first and last entrance

- Drive unit encased in extruded aluminium profile (155 mm height)

- Single folder LW = 800mm to 1200mm, LH up to 2500mm

- Synchronous Bi-Folder LW = 1900mm to 2400mm, LH up to 2500mm

Activation		Entry:

Exit:

    - DORMA Prosecure Opti-Combi combined radar activation and threshold infrared safety sensor

    - Hard wired or wireless wall switch actuation satin stainless steel 150 x 150mm (Option)

    - Slimline jamb switch satin stainless steel 115 x 45mm (Option)

    - Link to access control (By others). DORMA require a normally open volt free contact momentarily closed on receipt of a valid signal from the access control system (Option)

Power Failure/Fire Alarm	Monitored battery back up system to automatically open the doors in the case of a power failure or upon a signal from the interfaced fire alarm system

Safety Devices

    - Self-regulating safety system monitoring all door movements including closing force.

    - Presence sensors monitoring the threshold area preventing the doors from closing on users

    - DORMA IRS 4 Safe monitored safety sensors to secondary closing edge of door leaf (Option)

    - Framed glazed safety barrier with toughened glass infills installed along the line of doors in the open position (Option)

    - Emergency Break glass (Option)

Locking Facility

- Electro - Mechanical Lock (Option)

- Manual hook lock (Option)

- Manual floor lock (Option)

- Emergency Break glass (Option)

Door leaves and operator cover

    - Thermally broken aluminium frames/profiles

    - Glazing - 28mm ISO DGU UG 1.0

    - Glazing - 28mm ISO DGU UG 3.0 (Option)

    - Aluminium Profile coating

      - Polyester Powder Coating (Option)

      - Silver Anodised (Option)

      - Stainless Steel (Option)

Applicable Standards	The installation shall comply with BS EN 16005

Electrical Requirements 	The electrical contractor shall provide a 240-volt AC mains spur to the right-hand side of the opening above and on the same face that each drive unit is fitted. The spur must be switched and fused with a central flex outlet faceplate. A 10 amp residual circuit breaker at the mains board and a 5-amp fuse at the spur shall protect the circuit.

Fire Alarm Requirements	The fire alarm specialist shall provide a normally open volt free contact that is closed on alarm. The contacts shall be terminated adjacent to the fused spurs

Real Time Remote	Dorvision GPRS based wireless system concealed within the operator; system shall

Monitoring System	monitor each door location remotely via the internet incorporating facility to lock / unlock doors, timed automatic locking, reset, diagnostic system check and to provide data capture on usage and performance (Option)